## Estimator
Mesta Electronics, Inc.
DPM ACTIVE FILTER SIZING ESTIMATOR | [7 empty] | 11020 Parker Dr. Pgh., PA 15642 800-535-6798 www.mesta.com
CUSTOMER INPUT
SYSTEM w/DPM
| Non-Linear Loads | [6 empty] | System with
| Total Non-Linear Loads HP: | 455 |  |  | SYSTEM w/o | System with | System with | 0% TDD
| % DC Bus Choke Reactance (Z_DC): | 4 |  |  | DPM | acceptable TDD | 0% TDD | & acceptable PF
| % Input Line Reactance (Z_LINE): | 0.5 |  | RMS Current: | 480.2389 | 441.9704 | 441.419 | 441.419
| Acceptable TDD: | 5 |  | Fundamental Current: | 441.419 | 441.419 | 441.419 | 441.419
| Acceptable Displacement PF: | 0.95 |  | Harmonic Current: | 189.1524 | 22.0709 | 0 | 0
|  |  |  | TDD%: | 42.851 | 5 | 0 | 0
|  |  |  | Reactive Current: | 197.3412 | 60.4322 | 56.2576 | 56.2576
| Linear Loads |  |  | DPM Current: | 0 | 167.0815 | 189.1524 | 189.1524
| Total Linear Motor Loads HP: | 0 |  | I_r: | 437.8194 | 437.8194 | 437.8194 | 437.8194
| Linear Motor Loads PF: | 0 |  | I_d: | 56.2576 | 56.2576 | 56.2576 | 56.2576
| Resistive Loads kW: | 0 |  | Power Factor: | 0.91167 | 0.99061 | 0.99185 | 0.99185
| Total Linear PF: | 0 |  |  | Estimated Size of Mesta DPM
[5 empty] | 189.1524 | amps
Select appropriate Mesta DPM model
based on this estimate.
| I_RMS: | 105.547 |  | Information presented here is for estimating purposes only and does not imply any guarantee of performance or results.
| TDD: | 42.851 |  | The Mesta DPM may not operate properly if any power factor correction capacitors, or line input filters, are installed on the load
| PF: | 0.91167 |  | side of the Mesta DPM current sensors.
| kW: | 79.999 |  | Consult factory for any questions regarding the presence of power factor correction capacitors, or line input filters, on your system.
| kVA: | 87.751 |  | All non-linear loads must have an input line reactor (min. 3%) or a DC link choke (min. 4%) to achieve desired system performance.
A THD (V) of less than 5% can be achieved if TDD (I) is less than 5%.
| %ZDC | %LINE | Ih(A) | %THD-F | P.F. | KW | KVA | IRMS | IF | R1 | IR | PAGE
| 0 | 2 | 55.2 | 56.242 | 0.8554 | 79.999 | 93.522 | 112.49 | 98.148 | 5.167 |  | 9-H3
| 0 | 3 | 43.5785 | 44.226 | 0.8942 | 80.008 | 89.474 | 107.62 | 98.535 | 5.0849 |  | 12-H2
| 0 | 4 | 37.847 | 38.201 | 0.9108 | 80.007 | 87.843 | 105.658 | 99.072 | 5.0141 |  | 10-H1
| 0 | 5 | 34.425 | 34.594 | 0.9167 | 79.999 | 87.27 | 104.97 | 99.511 | 4.95 |  | 12-H3
| 0 | 6 | 31.99 | 31.991 | 0.92021 | 79.998 | 86.935 | 104.566 | 99.999 | 4.888 |  | 10-H3
| 0 | 7 | 30.1325 | 29.964 | 0.9208 | 80.002 | 86.881 | 104.502 | 100.561 | 4.8278
| 0 | 8 | 28.6585 | 28.368 | 0.9204 | 80.001 | 86.917 | 104.545 | 101.024 | 4.7697
| 0 | 9 | 27.4537 | 27.038 | 0.9194 | 80.001 | 87.014 | 104.662 | 101.537 | 4.7134
| 0 | 10 | 26.326 | 25.798 | 0.9178 | 80.005 | 87.167 | 104.846 | 102.046 | 4.6575
| 0 | 11 | 25.4256 | 24.793 | 0.9159 | 80.002 | 87.348 | 105.064 | 102.551 | 4.6029
| 1 | 1 | 64.534 | 66.08 | 0.8177 | 79.996 | 97.871 | 117.72 | 97.658 | 5.2396 |  | 16-H3
| 1 | 2 | 46.575 | 47.581 | 0.8891 | 79.997 | 89.978 | 108.227 | 97.885 | 5.1717 |  | 15-H1
| 1 | 3 | 39.475 | 40.128 | 0.9102 | 79.997 | 87.888 | 105.713 | 98.373 | 5.0798 |  | 15-H2
| 1 | 4 | 35.426 | 35.801 | 0.91887 | 80.006 | 87.07 | 104.729 | 98.952 | 5.013 |  | 15-H3
| 1 | 5 | 32.809 | 32.996 | 0.9218 | 80.002 | 86.788 | 104.39 | 99.433 | 4.9507 |  | 16-H1
| 1 | 6 | 30.837 | 30.855 | 0.9231 | 79.999 | 86.663 | 104.24 | 99.942 | 4.8905 |  | 16-H2
| 1 | 7 | 29.316 | 29.186 | 0.92282 | 79.998 | 86.688 | 104.27 | 100.444 | 4.8311 | 96.223 | 5-H1
| 1 | 8 | 28.04 | 27.775 | 0.9219 | 80.001 | 86.78 | 104.38 | 100.954 | 4.7733 | 96.226 | 5-H2
| 1 | 9 | 26.976 | 26.585 | 0.92076 | 80.001 | 86.885 | 104.507 | 101.47 | 4.7164 | 96.226 | 5-H3
| 1 | 10 | 25.937 | 25.432 | 0.9189 | 79.999 | 87.057 | 104.713 | 101.986 | 4.6609 | 96.224 | 1-H1
| 1 | 11 | 25.122 | 24.512 | 0.9168 | 80.002 | 87.258 | 104.955 | 102.488 | 4.6062 | 96.227 | 1-H2
| 2 | 0.5 | 61.149 | 62.933 | 0.83576 | 79.998 | 95.719 | 115.132 | 97.164 | 5.2592 |  | 8-H2
| 2 | 1.5 | 44.718 | 45.795 | 0.89742 | 79.999 | 89.143 | 107.223 | 97.648 | 5.1784 |  | 8-H3
| 2 | 2 | 41.038 | 41.946 | 0.9072 | 80.002 | 88.185 | 106.07 | 97.835 | 5.1432 |  | 11-H3
| 2 | 3 | 36.5 | 37.138 | 0.9201 | 79.998 | 86.945 | 104.579 | 98.283 | 5.0767 |  | 9-H1
| 2 | 4 | 32.932 | 33.322 | 0.924 | 79.998 | 86.58 | 104.14 | 98.832 | 5.0135 |  | 12-H2
| 2 | 5 | 31.491 | 31.682 | 0.9262 | 80 | 86.374 | 103.892 | 99.397 | 4.9518 |  | 11-H2
| 2 | 6 | 29.936 | 29.978 | 0.9261 | 80.003 | 86.389 | 103.91 | 99.858 | 4.8916 | 96.229 | 3-H1
| 2 | 7 | 28.632 | 28.515 | 0.9252 | 80.003 | 86.471 | 104.009 | 100.409 | 4.8332 | 96.229 | 3-H2
| 2 | 8 | 27.48 | 27.2357 | 0.9238 | 80.002 | 86.602 | 104.166 | 100.897 | 4.7758 | 96.227 | 3-H3
| 2 | 9 | 26.522 | 26.155 | 0.92165 | 80.004 | 86.805 | 104.41 | 101.406 | 4.7197 | 96.23 | 4-H1
| 2 | 10 | 25.633 | 25.15 | 0.9196 | 80.002 | 86.996 | 104.64 | 101.922 | 4.6641 | 96.227 | 4-H2
| 2 | 11 | 24.818 | 24.227 | 0.91726 | 80.004 | 87.22 | 104.91 | 102.439 | 4.6093 | 96.23 | 4-H3
| 3 | 0.5 | 48.302 | 49.813 | 0.88794 | 80.001 | 90.097 | 108.37 | 96.966 | 5.2381 |  | 2-H2
| 3 | 1.5 | 39.79 | 40.796 | 0.91478 | 80 | 87.452 | 105.189 | 97.533 | 5.1699 |  | 2-H1
| 3 | 2 | 39.893 | 40.814 | 0.91935 | 80.003 | 87.021 | 104.67 | 97.743 | 5.1376 |  | 11-H1
| 3 | 3 | 34.363 | 34.986 | 0.92678 | 79.998 | 86.319 | 103.825 | 98.219 | 5.0745 |  | 1-H2
| 3 | 4 | 32.178 | 32.584 | 0.92825 | 79.99 | 86.173 | 103.65 | 98.754 | 5.013 |  | 11-H2
| 3 | 5 | 30.503 | 30.689 | 0.92895 | 80.041 | 86.163 | 103.637 | 99.394 | 4.95 |  | 3-H1
| 3 | 6 | 29.173 | 29.229 | 0.9277 | 79.996 | 86.231 | 103.72 | 99.808 | 4.894 | 96.22 | 1-H1
| 3 | 7 | 28.046 | 27.957 | 0.9264 | 79.998 | 86.356 | 103.72 | 100.32 | 4.8355 | 96.222 | 1-H2
| 3 | 8 | 27.038 | 26.81 | 0.9264 | 80 | 86.522 | 104.07 | 100.84 | 4.7784 | 96.225 | 1-H3
| 3 | 9 | 26.158 | 25.808 | 0.9226 | 80 | 86.713 | 104.3 | 101.357 | 4.7221 | 96.225 | 2-H1
| 3 | 10 | 25.338 | 24.87 | 0.92036 | 79.999 | 86.921 | 104.55 | 101.87 | 4.6667 | 96.225 | 2-H2
| 3 | 11 | 24.575 | 24 | 0.918 | 80.002 | 87.146 | 104.82 | 102.389 | 4.6118 | 96.225 | 2-H3
| 4 | 0.5 | 41.519 | 42.851 | 0.91167 | 79.999 | 87.751 | 105.547 | 96.892 | 5.2263 |  | 7-H1
| 4 | 1.5 | 36.603 | 37.563 | 0.92524 | 79.999 | 86.464 | 103.999 | 97.444 | 5.1643 |  | 7-H2
| 4 | 2 | 35.05 | 35.885 | 0.92726 | 79.997 | 86.273 | 103.77 | 97.673 | 5.134 |  | 13-H1
| 4 | 3 | 32.782 | 33.392 | 0.9314 | 79.998 | 85.89 | 103.309 | 98.173 | 5.0729 |  | 7-H3
| 4 | 4 | 31.09 | 31.493 | 0.93125 | 80.001 | 85.907 | 103.33 | 98.719 | 5.0129 |  | 13-H2
| 4 | 5 | 29.689 | 29.901 | 0.93103 | 79.996 | 85.923 | 103.349 | 99.293 | 4.9537 |  | 8-H1
| 4 | 6 | 28.557 | 27.59 | 0.9297 | 79.998 | 86.047 | 103.499 | 99.744 | 4.8948 | 96.223 | 1-H1
| 4 | 7 | 27.58 | 27.5 | 0.928 | 79.998 | 86.203 | 103.686 | 100.28 | 4.8371 | 96.223 | 1-H2
| 4 | 8 | 26.627 | 26.41 | 0.9261 | 80.004 | 86.389 | 103.91 | 100.81 | 4.78 | 96.23 | 1-H3
| 4 | 9 | 25.887 | 25.555 | 0.9239 | 79.999 | 86.586 | 104.147 | 101.3 | 4.7243 | 96.224 | 2-H1
| 4 | 10 | 25.034 | 24.514 | 0.9215 | 79.998 | 86.811 | 104.417 | 102.12 | 4.6687 | 96.223 | 2-H2
| 4 | 11 | 24.4 | 23.84 | 0.91905 | 80.002 | 87.048 | 104.703 | 102.347 | 4.614 | 96.227 | 2-H3
| 5 | 0.5 | 37.503 | 38.715 | 0.92404 | 79.999 | 86.575 | 104.134 | 96.869 | 5.2187 |  | 4-H1
| 5 | 1.5 | 34.426 | 35.349 | 0.93197 | 80.001 | 85.841 | 103.251 | 97.391 | 5.16 |  | 4-H3
| 5 | 2 | 33.312 | 34.118 | 0.93268 | 80 | 85.774 | 103.17 | 97.637 | 5.1307 |  | 13-H3
| 5 | 3 | 31.578 | 32.177 | 0.93453 | 79.998 | 85.603 | 102.964 | 98.138 | 5.0716 |  | 5-H1
| 5 | 4 | 30.232 | 30.638 | 0.93341 | 80 | 85.707 | 103.09 | 98.677 | 5.0127 |  | 14-H1
| 5 | 5 | 29.038 | 29.255 | 0.93261 | 80 | 85.78 | 103.178 | 99.257 | 4.9542 |  | 5-H2
| 5 | 6 | 25.426 | 25.501 | 0.93102 | 80.001 | 85.929 | 103.357 | 99.705 | 4.8961
| 5 | 7 | 25.426 | 25.365 | 0.92909 | 79.998 | 86.104 | 103.567 | 100.24 | 4.8388
| 5 | 8 | 25.426 | 25.232 | 0.927 | 80.003 | 86.303 | 103.806 | 100.769 | 4.7821
| 5 | 9 | 24.208 | 23.905 | 0.92466 | 80.005 | 86.524 | 104.072 | 101.267 | 4.7258
| 5 | 10 | 25.426 | 24.974 | 0.92222 | 80.002 | 86.749 | 104.343 | 101.809 | 4.6708
| 5 | 11 | 24.208 | 23.664 | 0.91963 | 79.998 | 86.99 | 104.632 | 102.299 | 4.6162

## Instructions
DPMTM (Active Filter) Sizing Estimator Instructions: | Mesta Electronics, Inc.
Enter the following parameters: | 800-535-6798
Non-Linear Loads | 11020 Parker Drive
1-Total Horsepower of all similar non-linear loads | N. Huntingdon, PA 15642
2-DC buss inductance % of non-linear loads (enter: 0, 1, 2, 3, 4 or 5)
3-Input AC line reactor % of non-linear loads (enter: .5, 1, 2, 3, 4, 5 or 6)
(Note: If DC buss inductance is less than 2% then the AC line reactance must be at least 2%)
4-Acceptable TDD (I) %
5-Acceptable power factor
Linear Loads
1-Total horsepower of all similar linear motor loads
2-Power factor of linear motor loads
3-Total kW of all resistive loads (power factor = 1.0)
To Calculate Results
Left mouse button click on “Return Values from Table” button
Left mouse button click on “Calculate DPM Size” button
Results
The program will display four sets of electrical system parameters based on different levels of correction
System W/O DPM
Displays estimates of the electrical system parameter without any correction
System with Acceptable TDD
Displays estimates of the electrical system parameters with the entered acceptable TDD (I) value
System with 0% TDD
Displays estimates of the electrical system parameters if 0% TDD (I) is achieved
System with 0% TDD and Acceptable Power Factor
Displays estimates of the electrical system parameters with 0% TDD and the entered acceptable Power Factor value.
Estimated size of Mesta DPM
Displays the estimated minimum size of the required Mesta DPM (Active filter)
The Mesta DPM model rating should be equal to or greater than the displayed value.
Note: If you have any questions regarding the use, or results, of the Mesta DPM sizing estimator please contact the Mesta factory for assistance.